## Abbreviations p1-2
Items | Description | Label Structure / Example | Notes and Rules | rev.
(sp) | SPACES | sp.fczz.nnnnn | "sp" = 2 digit space code "fc" = 2 digit facility code "zz" = 2 digit level code "nnnnn" = 5 digit sequence number for each "fczz"
EF | Entrance Facility | EF.MT01.00250 | 1. Main distribution room sequence numbers shall be unique.
EQ | Equipment Rack/Cabinet * | EQ.MT01.abcde * | All other sequence numbers shall restart with each level of the facility.
EQ | a. For a Rack/Cabinet/Demarc in a single room or near a common door: | EQ.MT-1234-T** | 2. Use existing names when available for handholes, manholes and | 18
EQ | b. For a Rack/Cabinet/Demarc near or attached to a STIA structural column | EQ.MT04_1.5S_J.8*** | cable vaults | 18
ER | Equipment Room | ER.MT06.02350
HH | Hand Hole | HH.PT08.00010 | * For EQ racks within STIA communications rooms, the 5 digit sequence number is as follows:
JT | Junction Tray | JT.MT04.00110 | sp.fczz.abcde
a = last digit of the room in which the rack or cabinet is located.
MD | Main Distribution Room | MD.MT04.00010 | a = "0" for racks, cabinets and wall fields not located in comm rooms
MH | Man Hole | MH.EX01.02540 | bc = the row(wall) designator in the room
PB | Pull Box | PB.AD09.08000 | de = the sequence designator (rack/vertical section) in the row(wall)
TC | Telecommunication Closet | TC.MT06.00280
|  |  | ** For EQ racks outside of STIA communications rooms (within a room or near a door), the facility code and sequence number is as follows: | 18
Following the "EQ." simply use the STIA door ID that houses (or is nearest to) the Rack/Cabinet.
NOTE: Where two or more racks are side by side, then label each rack as follows: EQ.MT-1234-T.1 and EQ.MT-1234-T.2 (and so on)
*** For EQ racks or cabinets outside of STIA communications rooms (near or attached to a STIA structural column), the facility code and sequence number is as follows:
Following the FIRST underscore (_) place the specific North-South Gridline. Under the SECOND underscore (_) place the specific West-East gridline.
NOTE: Where two or more racks are side by side of column, then label each rack as follows: EQ.MT04.1_1.5S_J.8 and EQ.MT04_1.5S_J.8 (and so on)
WA | Work Area | WA.MT01.00250
WF** | Wall Field ** | WF.MT06.10101.20
** For WF (wall-fields), the 5 digit sequence number is as follows:
** |  |  | sp.fczz.abcde.pp | 16
sp.fczz.abcde.pp
a = last digit of the room in which the rack or cabinet is located.
a = "0" for racks, cabinets and wall fields not located in comm rooms
bc = wall number
When standing at communication room door, the wall with the door is '01'. Wall numbers are incremented by adding 1 as you go around the room clockwise. For example, in a room with 4 walls, the left hand wall is '02', the wall opposite the door is numbered '03', the wall to the right of door is '04'.
RHG | Remote Hub Group (AT&T / Cingular wireless project only) |  | de = horizontal position of the wall field
pp = vertical position on wall (similar to rack position)
(ptw) | PATHWAYS |  | "ptw" = 3 digit pathway code "fc" = 2 digit facility code "nnnnn" = 5 digit sequence number for each "fc"
| 1st Line (2nd Line blank) | ptw.fc.nnnnn | ( for Cable Tray and Conduit only )
| 1st Line | ptw.fc.nnnnn | ( for Innerduct only)
| 2nd Line | sp.fczz.nnnnn-sp.fczz.nnnnn | ( for Innerduct only)
AT | Antenna | AT.CA05.00001 | For AWS airport-wide project, nnnnn is as follows:
nnnnn = 00rat, where "r" = remote hub group and "at" = antenna number.
Example: RHG 9, antenna 5 will have a sequence number of "00905".
CDB | Conduit, Backbone | CDB.MT.00001 | 1. For a pathway occupying two or more facilities, use the fc code
CDO | Conduit, Other | CDO.MT.00001 | with the facility containing the majority of the run.
CDT | Conduit, Telecom | CDT.CD.08023
CTB | Cable Tray, Backbone | CTB.CA.00201 | 2. For the spaces (sp's) in the second line nomenclature for Innerduct,
CTT | Cable Tray, Telecom | CTT.MT.28034 | use the end locations (sp's) of the cable (source and destination).
DDO | Innerduct, Other | DDO.CD.08023
DDT | Innerduct, Telecom | DDT.PT.39885
SLT | Sleeve, Telecom | SLT.CB.98876
**
"cb" = 2 digit cable type code
"st" = 2 digit cable subtype code
"fc" = 2 digit facility code
"zz" = 2 digit level code
"nnnnn" = 5 digit sequence number
"sf" = 2 digit suffix number for 'split' cable groups
(cb) | CABLE |  | ( * used with cable-id only)
| Cable ID: 1st Line (2nd Line blank) | cb.st.fc.nnnnn.sf * | ( for Non Composite Backbone or Other cables )
| Cable ID: 1st & 2nd Line | cb.st.fc.nnnnn.ss.sf * | ( for Composite Backbone or Other cables )
| Cable ID: 1st Line (2nd Line blank) | cb.st.fczz.nnnnn | ( for Horizontal cables )
| Cable ID: 1st & 2nd Line | cb.st.fczz.nnnnn.ss | ( for Composite Horizontal cables )
CB | Copper Cable, Backbone ** | CB.UT.CA.01001 | 1. Backbone cable do not include the zz (level) code; all other cables do.
CH | Copper Cable, Horizontal | CH.UT.MT01.01345
CO | Copper Cable, Other ** | CO.CX.CD01.01002 | 2. The 3rd line on the cable label provides the from and to identifier
FB | Fiber Cable, Backbone ** | FB.SM.MT.01003 | For all non-horz. cables, sp.fczz.nnnn is the unique space identifier.
FB | Fiber Cable, Backbone (Composite cable) ** | FB.XM.MT.01004.M6/SM | For horizontal cables, th.fczz.nnnnn is the unique termination
FH | Fiber Cable, Horizontal | FH.M6.MT02.01234 | hardware identifier.
FH | Fiber Cable, Horizontal (Composite cable) | FH.XM.MT02.01234.M6/SM
FO | Fiber Cable, Other ** | FO.SM.MT03.01005 | 3. For a cable occupying two or more facilities or levels, use the fczz code
FO | Fiber Cable, Other (Composite cable) ** | FO.XM.MT03.01005.MS/SM | where the cable originates or where most of the cable resides.
** | Cables that require unique sequence numbers
(st) | Cable Subtype | (ss) Cable Subsubtype
CC | Copper Cross Connect
CX | Co-axial
FX | Fiber Station Cable
JD | Jumper, Duplex, Fiber
JS | Jumper, Simplex, Fiber
M5 | Multimode, 50 Micron | M5 Multimode, 50 Micron
M6 | Multimode, 62.5 Micron | M6 Multimode, 62.5 Micron
MS | Multi-conductor, Shielded (SM)
MU | Multi-conductor, Unshielded (MU)
RX | Radiating Coax
SA | Single Mode, Allwave | SA Single Mode, Allwave
SD | Single Mode, Depressed Clad | SD Single Mode, Depressed Clad
SM | Single Mode, Matched Clad | SM Single Mode, Matched Clad
ST | Shielded Twisted Pair
U3 | CAT 3 Unshielded Twisted Pair
U5 | CAT 5 Unshielded Twisted Pair
U6 | CAT 6 Unshielded Twisted Pair
US | Universal Station Cable
UT | Uncategorized Unshielded Twisted Pair
VP | Voice Paging System
WC | Wireless System Coax
XM | Composite Cable
(th) | TERMINATION HARDWARE | th.fczz.nnnnn | "th" = 2 digit termination hardware code "fc" = 2 digit facility code "zz" = 2 digit level code "nnnnn" = 5 digit sequence number for each "fczz"
CD | Copper Data Jack | CD.MT06.02700
CM | Intercom | CM.MT06.12250
CU | Copper Universal Outlet | CU.SS05.09000
CV | Copper Voice Jack | CV.AD09.09000
FD | Fiber Data Jack | FD.MT05.03000
FV | Fiber Voice Jack | FV.AD09.00900
PP | Protector Panel | PP.AD06.15550
TV | Television Jack | TV.MT05.01210
VP | Voice Paging | VP.MT05.01234
**
(t) | Cross Connects | t.stc. fczz.nnnnn.xx | "t" = cross-connect type code "stc" = sub-type code "fczz" = the space where the cross-connect is located "nnnnn" = 5 digit sequence number "xx" = 2 digit sequence number in rack(wall)
M | Main Cross Connnects | M.FPP.MT01.00001.01
I | Intermediate Cross Connection | I.CPP.MT01.00001.01
H | Horizontal Cross Connects | H.CPB.MT01.00001.01
**
(stc) | Cross Connect Subtype
CES | Copper Network Switch , or Channel Bank | I.CES.MT04.20201.23 | * For all cross connect subtypes, the 5 digit seq. no. will be as follows:
CPB | Copper Cross-Connect, Punchdown Type (66, 110) | I.CPB.MT04.20401.01 H.CPB.MT04.20402.02 | t.stc.fczz.abcde
CPP | Copper Patch Panel, Jack Type (RJ45) | H.CPP.MT04.20103.09 | a = last digit of the room which the (Cross-Connect sub-type) is located in.
CPT | Copper Cross-Connect, Strip/Block Type | H.CPT.MT04.20404.01 | bc = the row / wall designator in the room
de - the sequence designator (rack / verticle section) in the row / wall
FES | Fiber Network Switch |  | pp - the termination device position in the bcde location
FPP | Fiber Optic Patch Panel | M.FPP.MT01.20402.20
FSS | Fiber Splice Shelf | M.FSS.MT01.20406.10
XPP | Hybrid Patch Panel with Copper RJ45 and Fiber Optic Ports * | H.XPP.MT04.20405.01
**
TV | Video mutliplexer, or Video amplifier | TV.SS00.10102.21 | (this device does not have a cross-connect or sub-type code) | 18
PC | Rack-mounted computer | PC.SS00.10102.18 | (this device does not have a cross-connect or sub-type code) | 18
(sc) | SPLICES | sc.fczz.nnnnn | "sc" = 2 digit splice code "fc" = 2 digit facility code "zz" - 2 digit level code "nnnnn" = 5 digit sequence number
CS | COPPER SPLICE | CS.MT01.12300
FS | FIBER SPLICE | FS.MT02.34500
**
(gs) | GROUNDING SYSTEM | gs.fczz.nnnnn | "gs" = 2 digit grounding system code "fc" = 2 digit facility code "zz" - 2 digit level code "nnnnn" = 5 digit sequence number
BC | BONDING CONDUCTOR (BC) | BC.MT01.12500 | 1. TIA standard abbreviations
EG | EQUIPMENT BONDING CONDUCTOR (EBC) | EG.MT01.12500
GB | GROUNDING BUSBAR (GB) | GB.MT01.12500
TG | TELECOM GROUNDING BUSBAR (TGB) | TG.MT01.12500
TM | TELECOM MAIN GROUNDING BUSBAR (TMGB) | TM.MT01.12500
**

## Abbreviations p3
CODES | [5 empty] | rev.
Code (fc) | FACILITIES | (nnnnn) | SEQUENCE NUMBERS
AD | Admin Building | nnnnn | Various length sequence number with leading zeros.
CA | Concourse A
CB | Concourse B
CC | Concourse C
CD | Concourse D
CT | Central Terminal
EX | Exterior (see "Exterior Facilities" worksheet).
MT | Main Terminal
NS | North Satellite
NZ | North Toll Plaza
PT | Parking Terminal
OT | Office Tower
SS | South Satellite
FACILITY LEVELS
Code (zz) | MAIN TERMINAL (MT), and | Code (zz) | ADMIN BUILDING (AD) | Code (zz) | PARKING TERMINAL (PT)
SOUTH ESPLANADE (SE)
|  | 09 | Ninth Floor | 09 | Ninth Floor
|  | 08 | Eighth Floor | 08 | Eighth Floor
07 | Mechanical Penthouse | 07 | Seventh Floor | 07 | Seventh Floor
06 | Mezzanine | 06 | Sixth Floor | 06 | Sixth Floor
05 | Concourse (Ticketing) | 05 | Fifth Floor | 05 | Fifth Floor
04 | Ramp (Bridge) | 04 | Fourth Floor | 04 | Fourth Floor
03 | Baggage Claim | 03 | Third Floor | 03 | Third Floor
02 | Interstitial space / GTX Tunnel | 02 | Second Floor | 02 | Second Floor
01 | Transit (STS) | 01 | Not Used | 01 | First Floor
00 | Utility Tunnel | 00 | Ground | 00 | Basement
Code (zz) | CONCOURSE A (CA) | Code (zz) | CONCOURSE B (CB) | Code (zz) | CONCOURSE C (CC)
07 | Mechanical Penthouse | 07 | Mechanical Penthouse | 07 | Mechanical Penthouse
06 | Mezzanine |  |  | 06 | Mezzanine
05 | Concourse (Ticketing) | 05 | Concourse (Ticketing) | 05 | Concourse (Ticketing)
04 | Ramp (Bridge)
03 | Baggage Claim | 03 | Ramp (Bridge) | 03 | Ramp (Bridge)
02 | Interstitial Space
01 | Transit (STS) | 01 | Transit (STS) | 01 | Transit (STS)
Code (zz) | CONCOURSE D (CD) | Code (zz) | NORTH SATELLITE (NS) | Code (zz) | SOUTH SATELLITE (SS)
07 | Mechanical Penthouse | 07 | Mechanical Penthouse | 07 | Mechanical Penthouse
05 | Concourse (Ticketing) | 05 | Concourse (Ticketing) | 05 | Concourse (Ticketing)
|  |  |  | 04 | International Corridor
03 | Ramp (Bridge) | 03 | Ramp (Bridge) | 03 | Ramp (Bridge)
|  |  |  | 02 | Mezzanine (FIS)
01 | Transit (STS) | 01 | Transit (STS) | 01 | Transit (STS)
|  |  |  | 00 | Tunnel (Basement)
Code (zz) | CENTRAL TERMINAL (CT) | Code (zz) | NORTH TOLL PLAZA (NZ) | Code (zz) | EXTERIOR FACILITIES
(see 'Exterior Facilities' worksheet)
07 | Mechanical Penthouse
06 | Mezzanine |  |  | (levels vary by exterior facility)
05 | Concourse (Ticketing)
04 | Ramp (Bridge)
03 | Baggage Claim
|  | 02 | Floor 2
01 | Transit (STS) | 01 | Floor 1 | 01 | Grade Level
Code (zz) | OFFICE TOWER (OT) | Code (zz) | C1 BUILDING (C1) | Code (zz)
12 | Penthouse Level | TBD
11 | Office Level 5
10 | Office Level 4
09 | Office Level 3
08 | Office Level 2
07 | Office Level 1
06 | Mezzanine

## Sequence Numbers
Cable Management Sequence Number Assignements and Guidelines
I. Backbone and other (tie) Cables:
| 1. Backbone cables will have unique sequence numbers across all airport facilities; thereore they will never restart. |  |  |  |  | Rev 15
1. The following backbone cable sequence numbers have been reserved as of August 4, 2004:
|  | Reserved for Existing Backbone Cables | 00xxx
|  | Reserved for CIBS Backbone Cables (FO & CU) | 01xxx
|  | Reserved for STEP Backbone Cables | 02xxx
|  | Reserved for C4 Backbone Cables | 03xxx
|  | Reserved for CTE Backbone Cables | 04xxx
|  | Reserved for Tenant Demarc Backbone Cables | 05xxx
|  | Reserved for (URS Projects) Backbone Cables | 06xxx
|  | Reserved for 800 MHz Radio System Backbone Cables | 07xxx
|  | Reserved for Cingular Backbone Cables | 08001 through 08010
|  | Un-Allocated | 08011 through 08500
|  | Reserved for CCTV cameras / backbone cables | 08501 through 08900 | Rev 18
|  | Un-Allocated | 08901 through 99000 | "
|  | Reserved for Delta ticket counter project. | 99001-99199
|  | Reserved for Small/Misc.Project Cables | 99201 - 99xxx
II. Horizontal Cables:
1. Horizontal cables will have unique sequence numbers within each floor level of a particular facility but will restart with each new floor level of a facility, and will restart for each new facility.
2. Horizontal and Backbone cable sequence numbers do not require inter-coordination and may overlap.
| 3. All voice circuit sequence numbers must be within the range: |  |  | 00001 - 49999
| 4. All data circuit sequence numbers must be within the range: |  |  | 50001 - 99999
A. Horizontal cable sequence numbers reserved for STEP project, applies to facility codes “CA” and “OT”:
· Voice circuit range 00001 to 39000 (Start at 00001 and work up)
· Data Circuit Range 50001 to 77999 (Start at 50001 and work up)
B. Horizontal cable sequence numbers for C4 project, applies to facility code “CA”:
· Voice circuits 45001 – 49000 (Start at 45001 and work up)
· Data Circuits 95001 - 99000 (Start at 95001 and work up)
C. Horizontal cable sequence numbers reserved for ACSU project. Applies to all facility codes.
This sequence number reservation applies to all horizontal cables and conduits in all facilities.
· Data/Control circuits range 80001 – 89999
· ACSU used sequence numbers in the 90000-92999 range for conduit work.
D. Horizontal Cable sequence numbers reserved for FMS (facility monitoring system) / SCADA. Applies to all horizontal cables and conduits in all facilities.
(Special note: This range of sequence numbers may be used for all cable conduit and termination devices)
· Data/Control Circuits 93001 – 94999
| E. Horizontal Cable sequence numbers reserved for CIBS and small misc. projects (except CUTE/FIMS & TWVPS). Applies to all Facilities excluding CA & OT. |  |  |  | Rev 17
· Voice: 00001 – 00099
· Voice circuit range 39000 through 39999 (reserved for URS projects).
· Data: 50001 - 50099
· Data circuit range 78000 through 78999 (reserved for URS projects).
Currently used assignments “Delta Ticket counter” applies to facility code MT.
· Voice: 00001 – 00048
· Data: 50001 – 50046
| F. Horizontal Cable sequence numbers reserved for CUTE/FIMS. Applies to all Facilities. |  |  |  | Rev 17
sequence number = abcde
| · Voice: | a = 0 for voice from communications room to consolidation point
a = 1 for voice from consolidation point to jack at gate
| · Data: | a = 5 for data from communications room to consolidation point
a = 6 for data from consolidation point to jack at gate
b = last digit of the communication room number corresponding to where the cables originate
cde = port number within a cluster of patch panels (I.e. - 001-024 for patch panel in top position; 025-048 for next down, etc.)
| G. Horizontal Cable sequence numbers reserved for TWVPS (terminal wide voice paging system). |  |  |  | Rev 17
Applies to all Facilities except "CA" and "OT".
· Data circuit range 60001 through 69999

## Misc. Locations
Rev 18 - Misc. Locations
The following locations are to be used on a case-by-case basis only:
CMS Location ID | Location Type | Comments
WA.CB.CNN.CATV | WA (Work Area) | Various CNN-owned CATV amplifiers in Concourse 'B'
WA.CC.CNN.CATV | WA (Work Area) | Various CNN-owned CATV amplifiers in Concourse 'C'
WA.CD.CNN.CATV | WA (Work Area) | Various CNN-owned CATV amplifiers in Concourse 'D'
WA.MT.CNN.CATV | WA (Work Area) | Various CNN-owned CATV amplifiers in Main Terminal
WA.SS.CNN.CATV | WA (Work Area) | Various CNN-owned CATV amplifiers in South Satellite
WA.NS.CNN.CATV | WA (Work Area) | Various CNN-owned CATV amplifiers in North Satellite
EF.CA03.MH-H | EF (Entrance Facility) | Manhole 'H' Enters Utilidor @ column A65
(various external facilities) | n/a | See 'Exterior Facilities' worksheet tab.
BDA.800.CTE | BDA | 800 MHz system BDA in CTE basement | Rev 18

## Exterior Facilities
Rev 18 - Facilities exterior to STIA complex.
The following facility codes are to be used in the "from-to" position of the cable label, and also for "facility code" portion of the cable label.
Facility Description | Facility Code | Equipment Rooms
Air Cargo 4 | AC4
Alaska Hangar | AS1
Avia Transit Plex | AV1
Fire Dept. SAC Building | FD1
Gate E45 | E45
New FAA Tower | AT | ER.AT01.00001 | ER.AT15.00001
North Cruise Lot | NCL |  |  | Rev 18
North Main Substation | NMS
Northwest Hangar | NWH
Rental Car Facility | RC |  |  | Rev 18
South Fuel Farm | SFF
South Main Substation | SMS
Sound Transit Station | ST |  |  | Rev 18
South Tunnel Entrance | ST1
Example cable label (from MDR-2 to North Main Substation):
MD.MT01.00002-NMS
Example cable label (from MDR-1 to New FAA Tower, 1st Floor):
MD.MT04.00001-ER.AT01.00001

## Tenant Demarc Box
MT-01 Typical Tenant |  |  |  | Project# |  |  |  |  | POS Drawing# | STIA-TO
Tenant Facility Code (fc) = | MT |  | (Example shown) | Yellow highlighted areas are entered by the designer.
POS Communications Room ID = | ER.CA04.00001 |  | (Example shown)
sp = | EQ |  | (Example shown - typically "EQ" or "WF")
Tenant level code zz =
Communications room Facility Code (fc) = | CA
Communications room level code = | 04
nnnn = | 5011 | Starting Sequence |  | (TEXT IN RED FONT IS ENTERED BY POS - EXAMPLE SHOWN).
Below Data MUST be on each Cable Jacket: 1st line - 2nd Line (when noted) - 3rd Line
|  |  | CABLE TYPE: |  |  |  |  | BACKBONE CABLE LABEL (Label both ends of cable.)
[5 empty] | 1ST LINE: |  | 2ND LINE: |  | 3RD LINE:
POS TENANT DEMARC. BOX | [8 empty] | (COMM. RM END) | (DEMARC END) | POS COMMUNICATIONS ROOM:
(EXAMPLES SHOWN):
DEMARC BOX LABEL: | POS COMMUNICATIONS DEMARC | [11 empty] | COMM. ROOM |  | ER.CA04.00001
EQ.MT.05011
WALL FIELD
RG6 MULTI-PORT TAP LABEL
WF.CA.2bcde
RG6 PATCH DEVICE LABEL: | I.CXP.MT.05011.40 |  | RG6/U** | CB.CX.MT.05011 |  |  | (BLANK) |  | ER.CA04.00001 | -EQ.MT.05011 | TAP#:
(as required) | [10 empty] | 1
**NOTE: The RG6 cable does not need to be provided for communications rooms outside of Concourse 'A' or CTE.
RACK #:
abcd3
RJ45 PATCH PANEL LABEL: | I.CPP.MT.05011.30 | [9 empty] | CAT 6 (RJ-45) PATCH PANEL #
[11 empty] | PORT #: |  |  | I.CPP.CA04.'abcd3'.XX
|  |  | CAT 6, 4 PAIR | CB.U6.CA.05011 |  |  | (BLANK) |  | ER.CA04.00001 | -EQ.MT.05011 | 1
|  |  | CAT 6, 4 PAIR | CB.U6.CA.05012 |  |  | (BLANK) |  | ER.CA04.00001 | -EQ.MT.05011 | 2 | Below: Example of label on front of cPP
|  |  | CAT 6, 4 PAIR | CB.U6.CA.05013 |  |  | (BLANK) |  | ER.CA04.00001 | -EQ.MT.05011 | 3 | 05011 | 05012 | 05013 | 05014 | 05015 | 05016
|  |  | CAT 6, 4 PAIR | CB.U6.CA.05014 |  |  | (BLANK) |  | ER.CA04.00001 | -EQ.MT.05011 | 4 | MT-01 Typical Tenant
|  |  | CAT 6, 4 PAIR | CB.U6.CA.05015 |  |  | (BLANK) |  | ER.CA04.00001 | -EQ.MT.05011 | 5
|  |  | CAT 6, 4 PAIR | CB.U6.CA.05016 |  |  | (BLANK) |  | ER.CA04.00001 | -EQ.MT.05011 | 6
110 PUNCH-DOWN BLOCK LABEL: | I.CPB.MT.05011.20 | [9 empty] | 110 PUNCH-DOWN BLOCK #:
CKT #'S:
|  |  | CAT 5, 25 PAIR | CB.U5.CA.05011 |  |  | (BLANK) |  | ER.CA04.00001 | -EQ.MT.05011 | (1-25)X |  |  | I.CPB.CA04.'abcde'.XX
RACK #:
abcd1
FIBER OPTIC PATCH PANEL LABEL: | I.FPP.MT.05011.10 | [9 empty] | FIBER OPTIC PATCH PANEL #:
I.FPP.CA04.'abcd1'.XX
PORT #:
|  |  | SINGLEMODE FIBER | FB.SM.CA.05011 |  |  | (BLANK) |  | ER.CA04.00001 | -EQ.MT.05011 | 1
|  |  | OPTIC, 6 STRAND | [7 empty] | 2 | Below: Example of label Inside front FOPP door
[11 empty] | 3 | 1 | thru | 6 | FB.SM.CA.05011
[11 empty] | 4 |  | MT-01 Typical Tenant
5
6
PORT #:
|  |  | MULTIMODE FIBER | FB.M6.CA.05011 |  |  | (BLANK) |  | ER.CA04.00001 | -EQ.MT.05011 | 7
|  |  | OPTIC, 6 STRAND | [7 empty] | 8 | Below: Example of label Inside front FOPP door
|  |  | 62.5 MICRON | [7 empty] | 9 | 7 | thru | 12 | FB.M6.CA.05011
[11 empty] | 10 |  | MT-01 Typical Tenant
11
12
NOTES:
1.) 'abcde' = Rack or Wall Field ID. 'a' = last digit of Comm. Room ID; 'e' = rack #
2.) 'XX' = Rack mounting hieght location ID
** Coordinate with POS (Mike Schuman or Gary Mullin) for communication room rack layout and location. **

## Room Names
Communications Room Names (not including Concourse 'A')
CMS Space ID | Fac. Code | Fac.Code Descr | Level Code | Level Code Descr | Alt Name | Proj Name | Drawing
sp.fczz.nnnnn | fc |  | zz
ER.AD03.00001 | AD | Old Admin Bldg. | 03 | Third Floor | Wang Room #387 | PDOC |  | Rev 18
ER.AD03.00002 | AD | Old Admin Bldg. | 03 | Third Floor | PDOC Comm Rm. #327 | PDOC |  | Rev 18
ER.AD04.00001 | AD | Old Admin Bldg. | 04 | Fourth Floor | PDOC Comm Rm.# 426A | PDOC
ER.AD08.00001 | AD | Old Admin Bldg./Tower | 08 | Eighth Floor | Tower 8th Floor Junction Rm. | Ramp Tower Upgrade | STIA 0429 E5.3R1
ER.AT01.00001 | AT | New FAA Tower | 01 | First Floor |  | n/a |  | Rev 18
ER.AT15.00001 | AT | New FAA Tower | 15 | Fifteenth Floor |  | n/a |  | Rev 18
ER.CB01.00001 | CB | Concourse B | 01 | Transit (STS) | Door #B1106TR - RHG 14 | Cingular / AT&T
ER.CB03.00001 | CB | Concourse B | 03 | Ramp | TC-B-1-R | CIBS | ES3.52
ER.CB03.00002 | CB | Concourse B | 03 | Ramp | TC-B-2-R | CIBS | ES3.51
ER.CB03.00003 | CB | Concourse B | 03 | Ramp | TC-B-3-R | CIBS | ES3.51
ER.CB03.00004 | CB | Concourse B | 03 | Ramp | SAC-B-1-R | ACSU | ES3.52
ER.CB03.00005 | CB | Concourse B | 03 | Ramp | SAC-B-2-R | ACSU | ES3.51
ER.CB07.00001 | CB | Concourse B | 07 | Penthouse | Sound Room# B-7081-P | TWVPS |  | Rev 18
ER.CC02.00001 | CC | Concourse C | 02 | Second Floor | C102 (TSA Comm. Room) | C1 | 0424
ER.CC03.00001 | CC | Concourse C | 03 | Ramp | TC-C-1-R | CIBS | ES3.53
ER.CC03.00002 | CC | Concourse C | 03 | Ramp | TC-C-2-R | CIBS | ES3.53
ER.CC03.00003 | CC | Concourse C | 03 | Ramp | TC-C-3-R | CIBS | ES3.54
ER.CC03.00004 | CC | Concourse C | 03 | Ramp | SAC-C-1-R | ACSU | ES3.54
ER.CC03.00005 | CC | Concourse C | 03 | Ramp | SAC-C-2-R | ACSU | ES3.53
ER.CC05.00001 | CC | Concourse C | 05 | Concourse | C315 (Port Comm. Room) | C1 | 0424
ER.CC05.00002 | CC | Concourse C | 05 | Concourse | C302 (TSA Server Room) | C1
ER.CC06.00001 | CC | Concourse C | 06 | Mechanical Penthouse | TC-C-4-M | CIBS | ES3.94
ER.CC07.00001 | CC | Concourse C | 07 | Penthouse | Sound Room #C-7041-P | TWVPS |  | Rev 18
ER.CD03.00001 | CD | Concourse D | 03 | Ramp | TC-D-1-R | CIBS | ES3.49
ER.CD03.00002 | CD | Concourse D | 03 | Ramp | TC-D-2-R | CIBS | ES3.50
ER.CD03.00003 | CD | Concourse D | 03 | Ramp | TC-D-3-R | CIBS | ES3.50
ER.CD03.00004 | CD | Concourse D | 03 | Ramp | TC-D-4-R | CIBS | ES3.50
ER.CD03.00005 | CD | Concourse D | 03 | Ramp | SAC-D-1-R | ACSU | ES3.49
ER.CD07.00001 | CD | Concourse D | 07 | Penthouse | Sound Room# D-7019-P | TWVPS |  | Rev 18
ER.CT01.00001 | CT | Central Terminal | 01 | Transit (STS) | TC-BN | CTE | ES3.07
ER.CT04.00001 | CT | Central Terminal | 04 | Bridge (Ramp) | TC-RN | CTE | ES3.47
ER.CT04.00002 | CT | Central Terminal | 04 | Bridge (Ramp) | TC-RS | CTE | ES3.47
ER.CT06.00001 | CT | Central Terminal | 06 | Mezzanine | TC-2N | CTE | ES3.87
ER.CT06.00002 | CT | Central Terminal | 06 | Mezzanine | TC-2S | CTE | ES3.87
ER.MT01.00002 | MT | Main Terminal | 01 | Transit (STS) | SAC-MT-1-TR | ACSU | ES3.09
ER.MT01.00003 | MT | Main Terminal | 01 | Transit (STS) | SAC-MT-4-TR | ACSU | ES3.05
ER.MT01.00004 | MT | Main Terminal | 01 | Transit (STS) | CER | ACSU | ES3.08
ER.MT04.00001 | MT | Main Terminal | 04 | Bridge | TC-MT-1-BR | CIBS | ES3.45
ER.MT04.00002 | MT | Main Terminal | 04 | Bridge | TC-MT-2-BR | CIBS | ES3.46
ER.MT04.00003 | MT | Main Terminal | 04 | Bridge | TC-MT-3-BR | CIBS | ES3.48
ER.MT04.00004 | MT | Main Terminal | 04 | Bridge | TC-MT-4-BR | CIBS | ES3.49
ER.MT04.00005 | MT | Main Terminal | 04 | Bridge | SAC-MT-5-G | ACSU | ES3.48
ER.MT04.00006 | MT | Main Terminal | 04 | Bridge | SAC-MT-6-G | ACSU | ES3.47
ER.MT06.00001 | MT | Main Terminal | 06 | Mezzanine | TC-MT-1-M | CIBS | ES3.85
ER.MT06.00002 | MT | Main Terminal | 06 | Mezzanine | TC-MT-2-M | CIBS | ES3.86
ER.MT06.00003 | MT | Main Terminal | 06 | Mezzanine | TC-MT-3-M | CIBS | ES3.88
ER.MT06.00004 | MT | Main Terminal | 06 | Mezzanine | TC-MT-4-M | CIBS | ES3.88
ER.MT07.00001 | MT | Main Terminal | 07 | Penthouse | Radio Penthouse | Radio
ER.NS03.00001 | NS | North Satellite | 03 | Ramp | TC-NS-1-R | CIBS | ES4.33
ER.NS03.00002 | NS | North Satellite | 03 | Ramp | TC-NS-2-R | CIBS | ES4.34
ER.NS03.00003 | NS | North Satellite | 03 | Ramp | SAC-NS-1-R | ACSU | ES4.34
ER.NZ02.00001 | NZ | North Toll Plaza | 02 | Floor 2 | TC-PT2-NT | CIBS | ES4.66
ER.PT04.00001 | PT | Parking Terminal | 04 | Fourth Floor | ACC-EX (old) | CIBS | ES4.64
ER.PT09.00001 | PT | Parking Terminal | 09 | North Elevator Penthouse | Base Station Hotel | Cingular
ER.SS00.00001 | SS | South Satellite | 00 | Tunnel (Basement) | TC-SS-1-BS | CIBS | ES4.41
ER.SS01.00001 | SS | South Satellite | 01 | Transit (STS) | ER-CUTE | CIBS | ES4.43
ER.SS02.00001 | SS | South Satellite | 02 | Mezzanine (FIS) | TC-SS-2-M | CIBS | ES4.46
ER.SS03.00001 | SS | South Satellite | 03 | Ramp | TC-SS-3-R | CIBS | ES4.47
ER.SS03.00002 | SS | South Satellite | 03 | Ramp | TC-SS-4-R | CIBS | ES4.48
ER.SS03.00003 | SS | South Satellite | 03 | Ramp | SAC-SS-1-R | ACSU | ES4.48
MD.AD00.00004 | AD | Admin Building | 00 | Ground | MDR-4 / MTR | CIBS | ES3.47
MD.CA01.00003 | CA | Concourse A | 01 | Transit (STS) | MDR-3 | CIBS | ES3.04
MD.MT01.00002 | MT | Main Terminal | 01 | Transit (STS) | MDR-2 | CIBS | ES3.09
MD.MT04.00001 | MT | Main Terminal | 04 | Bridge | MDR-1 | CIBS | ES3.46
TC.PT02.00001 | PT | Parking Terminal | 02 | Second Floor | TC-PT1-F2 | CIBS | ES4.62
ER.RC01.00001 | RC | Rental Car Facility | 01 | First Floor | n/a | Rental Car Facility |  | Rev 18
ER.RC01.00002 | RC | Rental Car Facility | 01 | First Floor | n/a | Rental Car Facility |  | Rev 18
ER.RC02.00001 | RC | Rental Car Facility | 02 | Second Floor | n/a | Rental Car Facility |  | Rev 18
ER.RC02.00002 | RC | Rental Car Facility | 02 | Second Floor | n/a | Rental Car Facility |  | Rev 18
ER.RC03.00001 | RC | Rental Car Facility | 03 | Third Floor | n/a | Rental Car Facility |  | Rev 18
ER.RC03.00002 | RC | Rental Car Facility | 03 | Third Floor | n/a | Rental Car Facility |  | Rev 18
ER.RC04.00001 | RC | Rental Car Facility | 04 | Fourth Floor | n/a | Rental Car Facility |  | Rev 18
ER.RC04.00002 | RC | Rental Car Facility | 04 | Fourth Floor | n/a | Rental Car Facility |  | Rev 18
MD.RC05.00001 | RC | Rental Car Facility | 05 | Fifth Floor | MDR-RC | Rental Car Facility |  | Rev 18
ER.RC05.00001 | RC | Rental Car Facility | 05 | Fifth Floor | n/a | Rental Car Facility |  | Rev 18
ER.ST04.00001 | ST | Sound Transit Station | 04 | Bridge | TC-ST-1-M | Sound Transit Light Rail |  | Rev 18

## Conc. A Room Names
Concourse 'A' Communication Room Names (includes C4 Area & Airport Office Building )
CMS Space ID | Type | Fac. Code | Fac.Code Descr | Level Code | Level Code Descr | Seq. No. | Alt. Name
sp.fczz.nnnnn | sp | fc |  | zz |  | nnnnn
ER.CA04.00001 | ER | CA | Concourse A | 04 | Ramp (Bridge) | 00001 | IC-1
ER.CA04.00002 | ER | CA | Concourse A | 04 | Ramp (Bridge) | 00002 | IC-2
ER.CA04.00003 | ER | CA | Concourse A | 04 | Ramp (Bridge) | 00003 | IC-3
ER.CA03.00004 | ER | CA | Concourse A | 03 | Baggage Claim | 00004 | IC-4
ER.CA03.00005 | ER | CA | Concourse A | 03 | Baggage Claim | 00005 | IC-5
ER.CA03.00006 | ER | CA | Concourse A | 03 | Baggage Claim | 00006 | IC-6
ER.CA03.00007 | ER | CA | Concourse A | 03 | Baggage Claim | 00007 | IC-7
ER.CA03.00008 | ER | CA | Concourse A | 03 | Baggage Claim | 00008 | IC-8
ER.CA01.00001 | ER | CA | Concourse A - C4 area | 01 | STS Level | 00001 | MER-VD (Voice/Data)
ER.CA01.00002 | ER | CA | Concourse A - C4 area | 01 | STS Level | 00002 | MER-ES (Electronic Systems)
ER.CA01.00004 | ER | CA | Concourse A - C4 area | 01 | STS Level | 00004 | PS (Primary Server)
ER.CA01.00005 | ER | CA | Concourse A - C4 area | 01 | STS Level | 00005 | BS (Backup Server)
ER.CA01.00006 | ER | CA | Concourse A - C4 area | 01 | STS Level | 00006 | 911 ER (Equipment Room)
ER.CA01.00007 | ER | CA | Concourse A - C4 area | 01 | STS Level | 00007 | ACC ER
ER.CA01.00008 | ER | CA | Concourse A - C4 area | 01 | STS Level | 00008 | ST (Security-Techical)
ER.CA01.00009 | ER | CA | Concourse A - C4 area | 01 | STS Level | 00009 | TW (Technical Workshop)
ER.CA03.00011 | ER | CA | Concourse A | 03 | Baggage Claim |  | Cingular RHG-20 & 24
ER.OT06.00001 | ER | OT | Office Tower | 06 | Mezzanine | 00001 | IC-AV
ER.OT07.00001 | ER | OT | Office Tower | 07 | Office Level 1 | 00001 | IC-T1
ER.OT07.00002 | ER | OT | Office Tower | 07 | Office Level 1 | 00002 | NOC
ER.OT08.00001 | ER | OT | Office Tower | 08 | Office Level 2 | 00001 | IC-T2
ER.OT09.00001 | ER | OT | Office Tower | 09 | Office Level 3 | 00001 | IC-T3
ER.OT10.00001 | ER | OT | Office Tower | 10 | Office Level 4 | 00001 | IC-T4
ER.OT11.00001 | ER | OT | Office Tower | 11 | Office Level 5 | 00001 | IC-T5
ER.OT12.00001 | ER | OT | Office Tower | 12 | Penthouse | 00001 | IC-RF
MD.CA01.00003 | MD | CA | Concourse A | 01 | ST Level | 00003 | MDR-3
ER.CA04.00010 | ER | CA | Concourse A | 04 | Ramp (Bridge) | 00010 | Search Room
ER.CA05.00010 | ER | CA | Concourse A | 05 | Concourse (Ticketing) | 00010 | TSA Baggage Monitor Room

## Example-CMS Spreadsheet
EXAMPLE - CMS HORIZONTAL CABLE SCHEDULE :
NO. | PROJECT | STATUS | CABLE DESIGNATION | USE | CABLE TYPE/ALLOCATION | SOURCE ROOM | SOURCE DEVICE ID | PORT NO. | CABLE ID | DEST. ROOM | DESTINATION DEVICE TYPE | DESTINATION DEVICE ID | COMMENT
1 | C-1 | NEW | HORIZONTAL | DATA - GENERAL | CATEGORY 6 UTP | ER.CC02.00001 | H.CPP.CC02.10101.01 | 1 | CH.U6.CC02.50001 | C105 | DATA JACK | CD.CC02.00001 | DATA CONNECTION BETWEEN COMM. ROOM PATCH PANEL AND BAGGAGE CONTROL ROOM WALL JACK
2 | C-1 | NEW | HORIZONTAL | POWER/DATA - ACCESS CONTROL | 4-CONDUCTOR THHN 12AWG | ER.CC03.00005 | WF.CC05.10002 | NOT APPLIABLE | CO.UT.CC05.50007 | 5060 | INTERFACE TERMINATION BOX | WA.CC03.00001 | POWER/DATA CONNECTION BETWEEN CONTROLLER AND ITB
3 | C-1 | NEW | HORIZONTAL | POWER/DATA - ACCESS CONTROL | 2-CONDUCTOR 18AWG | ER.CC05.00001 | WF.CC05.10002 | NOT APPLIABLE | CO.UT.CC05.50018 | C321A | INTERFACE TERMINATION BOX | WA.CC05.00001 | POWER/DATA CONNECTION BETWEEN ACS CONTROLLER AND STAIR 3 DOOR
4 | C-1 | NEW | HORIZONTAL | DATA - ACCESS CONTROL | 2-STRAND MMF CABLE | ER.CC03.00005 | EQ.CC03.10101 | 7 | FH.M6.CC05.50019 | 5060 | INTERFACE TERMINATION BOX | FD.CC03.00001 | FUTURE DATA CONNECTION BETWEEN CONTROLLER AND ITB; SERVICE LOOPED AT ITB
5 | C-1 | NEW | HORIZONTAL | VIDEO | RG-6/U COAXIAL | ER.CC05.00001 | EQ.CC05.10202 | 5 | CH.CX.CC05.50001 | 318B | ONE (1) PTZ CAMERA | TV.CC05.00001 | VIDEO CONNECTION BETWEEN SECURITY MULTIPLEXER AND PTZ CAMERA
6 | C-1 | NEW | HORIZONTAL | POWER/DATA - INTERCOM | CATEGORY 6 UTP | ER.CC05.00001 | H.CPP.CC05.10101.01 | 2 | CO.UT.CC02.50026 | C105 | TWO (2) INTERCOM FIELD DEVICES | WA.CC05.00002 | POWER/DATA CONNECTION BETWEEN REMOTE INTERCHANGE AND TWO (2) INTERCOM FIELD DEVICES AT BAG. CONTROL ROOM DOOR
EXAMPLE - CMS BACKBONE CABLE SCHEDULE :
NO. | PROJECT | STATUS | CABLE DESIGNATION | USE | CABLE TYPE/ALLOCATION | SOURCE ROOM | SOURCE DEVICE ID | SOURCE PORT NO. | CABLE ID | DESTINATION ROOM | DESTINATION DEVICE ID | DESTINATION PORT NO. | COMMENT
1 | C-1 | NEW | FIBER OPTIC BACKBONE | VIDEO | 36-STRAND SM/36-STRAND MM COMPOSITE FIBER OPTIC CABLE | ER.CC05.00001 | H.FFP.CC05.10101.01, H.FFP.CC05.10101.04 | 1-36 | FB.XM.CC.06000.M6/SM | ER.CC02.00001 | H.FPP.CC02.10101.01, H.FPP.CC02.10101.02 | 1-24, 72-120 | NEW FO BACKBONE CABLE BETWEEN C102 AND C302
2 | C-1 | NEW | FIBER OPTIC BACKBONE | DATA | 96-STRAND SM/72-STRAND MM COMPOSITE FIBER OPTIC CABLE | MD.MT04.00001 | M.FPP.MT04.10307.10, M.FPP.MT04.10307.30 | TBD | FB.XM.CC.06001.M6/SM | ER.CC05.00001 | H.FPP.CC05.10101.01, H.FPP.CC05.10101.04 | 1-96; 1-72
3 | C-1 | NEW | COPPER BACKBONE | VOICE | 25-PAIR CATEGORY 5 UTP | MD.MT04.00001 | WF.MT04.10203.02 | 1-25 | CB.U5.CC.06002 | ER.CC05.00001 | M.CPB.CC05.50100.01 | 1-25 | C302 NO. 1 110-BLOCK
4 | C-1 | NEW | COPPER BACKBONE | VOICE | 25-PAIR CATEGORY 5 UTP | MD.MT04.00001 | WF.MT04.10203.02 | 26-50 | CB.U5.CC.06003 | ER.CC05.00001 | M.CPB.CC05.50100.01 | 26-50 | C302 NO. 1 110-BLOCK
5 | C-1 | NEW | COPPER BACKBONE | VOICE | 25-PAIR CATEGORY 5 UTP | MD.MT04.00001 | WF.MT04.10203.02 | 51-75 | CB.U5.CC.06004 | ER.CC05.00001 | M.CPB.CC05.50100.01 | 51-75 | C302 NO. 1 110-BLOCK
6 | C-1 | NEW | COPPER BACKBONE | VOICE | 25-PAIR CATEGORY 5 UTP | MD.MT04.00001 | WF.MT04.10203.02 | 76-100 | CB.U5.CC.06005 | ER.CC05.00001 | M.CPB.CC05.50100.01 | 76-100 | C302 NO. 1 110-BLOCK
7 | C-1 | NEW | FIBER OPTIC BACKBONE | DATA | 96-STRAND SM/72-STRAND MM COMPOSITE FIBER OPTIC CABLE | MD.MT01.00002 | M.FPP.MT01.20307.20, M.FPP.MT01.20307.30 | TBD | FB.XM.CC.06006.M6/SM | ER.CC05.00001 | H.FPP.CC05.10101.03, H.FPP.CC05.10101.04 | 1-96
8 | C-1 | NEW | FIBER OPTIC BACKBONE | DATA | 96-STRAND MM FIBER OPTIC CABLE | MD.MT04.00001 | M.FPP.MT04.10307.30, M.FPP.MT04.10307.40 | TBD | FB.M6.CC.06011 | C302 | H.FPP.CC05.00101 | 1-96 | CABLE ON PORT-OWNED DESTINATION EQUIPMENT IN TENANT ROOM