## LCP
| LIGHTING CONTROL PANEL SCHEDULE (SAMPLE) | [13 empty] | LCP A5-A20AC-1
480 | Y/ | 277 | VOLTS | NORMAL | POWER | [5 empty] | LOCATION: |  | MECH. PENTHOUSE, SECTOR 2
3 | -PHASE |  |  | PNL. MFR.: | [6 empty] | MOUNTING: |  | SURFACE
4 | -WIRE |  |  | CAT. NO.: | [6 empty] | FED FROM: |  | A2-L4-A20AC-1
|  |  |  | REF. DWG.: | EL2.52/E4.41 | [5 empty] | CONTROL PWR: |  | A2-L4-A20AC-1/20
RELAY | AREA |  |  |  | PANEL CIRCUIT # | ZONE | CNTRL | LOAD | LOAD | CNTRL | ZONE | AREA |  | PANEL CIRCUIT # |  | RELAY
NO. | [6 empty] | CODE | (kVA) | (kVA) | CODE | [5 empty] | NO.
1 | CONCOURSE GATE, SECTOR 2 |  |  |  | A5-L4-A20AC-1/1 | G13.2 | K3 | 0.352 | 0.392 | K3 | G25.2 | CONCOURSE GATE, SECTOR 2 |  | A5-L4-A20AC-1/2 |  | 2
3 | CONCOURSE GATE, SECTOR 2 |  |  |  | A5-L4-A20AC-1/1 | G14.2 | K3 | 0.352 | 0.392 | K3 | G26.2 | CONCOURSE GATE, SECTOR 2 |  | A5-L4-A20AC-1/2 |  | 4
5 | CONCOURSE GATE, SECTOR 2 |  |  |  | A5-L4-A20AC-1/3 | G19.2 | K3 | 0.784 | 0.588 | D | C1.2 | CONCOURSE, SECTOR 2 |  | A5-L4-A20AC-1/2 |  | 6
7 | CONCOURSE GATE, SECTOR 2 |  |  |  | A5-L4-A20AC-1/3 | G20.2 | K3 | 0.784 | 1.496 | A | C4.2 | CONCOURSE, SECTOR 2 |  | A5-L4-A20AC-1/4 |  | 8
9 | CONCOURSE EXTERIOR, SECTOR 2 |  |  |  | A5-L4-A20AC-1/5 | CE1.2 | E | 2.5 | 0.068 | A | C10.2 | CONCOURSE, SECTOR 2 |  | A5-L4-A20AC-1/6 |  | 10
11 | CONCOURSE EXTERIOR, SECTOR 2 |  |  |  | A5-L4-A20AC-1/7 | CE1.2 | E | 2.5 | 1.372 | B | C6.2 | CONCOURSE, SECTOR 2 |  | A5-L4-A20AC-1/6 |  | 12
13 | CONCOURSE EXTERIOR, SECTOR 2 |  |  |  | A5-L4-A20AC-1/9 | CE1.2 | E | 2.5 | 0.88 | B | C7.2 | CONCOURSE, SECTOR 2 |  | A5-L4-A20AC-1/6 |  | 14
15 | SOUTH HALL, SECTOR 2 |  |  |  | A5-L4-A20AC-1/10 | S26.3 | A | 0.96 | 2.88 | B | S29.3 | SOUTH HALL, SECTOR 2 |  | A5-L4-A20AC-1/11 |  | 16
17 | SOUTH HALL, SECTOR 2 |  |  |  | A5-L4-A20AC-1/10 | S27.3 | B | 0.832 | 2.07 | B | S25.3 | SOUTH HALL, SECTOR 2 |  | A5-L4-A20AC-1/8 |  | 18
19 | SOUTH HALL, SECTOR 2 |  |  |  | A5-L4-A20AC-1/10 | S28.3 | A | 0.21 | 2.016 | A | S24.3 | SOUTH HALL, SECTOR 2 |  | A5-L4-A20AC-1/12 |  | 20
21 | SOUTH HALL, SECTOR 2 |  |  |  | A5-L4-A20AC-1/10 | S21.3 | A | 0.366 | 2.5 | B | S54.4 | SOUTH HALL, SECTOR 2 |  | A5-L4-A20AC-1/13 |  | 22
23 | SOUTH HALL, SECTOR 2 |  |  |  | A5-L4-A20AC-1/15 | S54.4 | B | 2.5 | 2 | B | S54.4 | SOUTH HALL, SECTOR 2 |  | A5-L4-A20AC-1/17 |  | 24
25 | MECH. PENTHOUSE, SECTOR 2 |  |  |  | A5-L4-A20AC-1/19 | W/H | E | 0.18 |  |  |  | SPARE |  |  |  | 26
27 | SPARE | [10 empty] | SPARE |  |  |  | 28
29 | SPARE | [10 empty] | SPARE |  |  |  | 30
31 | SPARE | [10 empty] | SPARE |  |  |  | 32
33 | SPARE | [10 empty] | SPARE |  |  |  | 34
35 | SPARE | [10 empty] | SPARE |  |  |  | 36
37 | SPARE | [10 empty] | SPARE |  |  |  | 38
39 | SPARE | [10 empty] | SPARE |  |  |  | 40
41 | SPARE | [10 empty] | SPARE |  |  |  | 42
|  | CONTROL CODE DESCRIPTIONS: | [6 empty] | TOTALS: |  |  |  | REMARKS:
|  | A | = ON DURING DAY, ON AFTER HOURS | [5 empty] | 31.474 | kVA |  |  | REFERENCE [INSERT CONSULTANT NAME]
|  | B | = ON DURING DAY, OFF AFTER HOURS | [5 empty] | 37.8573 | AMPS |  |  | LIGHTING DRAWINGS AND SPECIFICATIONS
|  | C | = AUTO SWITCH FOR DAYLIGHT, ON AFTER HOURS | [9 empty] | FOR ZONE CONTROL INFORMATION.
|  | D | = AUTO SWITCH FOR DAYLIGHT, OFF AFTER HOURS
|  | E | = EXTERIOR BUILDING PHOTOCELL (ON DURING NIGHT)
|  | F | = ON AT ALL TIMES
|  | G | = EGRESS LIGHTING, ALWAYS ON
|  | H | = ON DURING DAY, OCCUPANCY SENSOR AFTER HOURS
|  | J | = BUILDING TIMER AND LOCALLY SWITCHED
|  | K | = AUTO SWITCH FOR DAYLIGHT, GATE SWITCH AFTER HOURS (K3=GATE SWITCH CLS.3)